| To: All Bidders | Date: 6/8/2026 |
| --- | --- |
| Quote: 26-0246 |  |
| Reference: PS Q517, 1 Beach 39th St, Queens NY - New Bldg |  |
| MEP Engineer: SCA |  |
| Based on Plans and Specs: M001.00 Thru M505.00 Dated: 03/31/2026 |  |

# Scope and Quotation

## A.M.E., Inc, is pleased to provide a quotation on the above project to provide Automated Temperature Controls system.

- SCOPE OF WORK – PREWAILING WAGE

- Front End Web Enabled BMS System

  - Furnish Network Level Control Panel

  - Furnish PC Workstation (School Operator Console )

  - Furnish BMS Server

  - Furnish POT (Laptop or Tablet)

  - Furnish UPS

  - Furnish 3-D Graphics

  - Furnish Necessary Training on New Controls

*INTEGRATION AND SOFTWARE FOR NYCDOE CENTRALISED HOST CONTROL STATION BY OTHERS – M406.00

*CONNECTION TO NYCDOE WAN BY OTHERS – M406.00

*AME WILL PROVIDE HORIZONTAL MS/TP BACNET AND LOW VOLTAGE WIRING FROM THE ITC BACNET WALL DATA ENCLOSURES TO BACNET FIELD TERMINAL DEVICES – M406.00

*AME SHALL TEST ALL HORIZONTAL CAT-6 CABLE RUNS AND PROVIDE TEST REPORT TO THE AUTHORITY – 15970-106

*THE DIVISION 16 ELECTRICAL SHALL PROVIDE ETHERNET CAT 6 BACNET CABLING PER THE REQUIREMENTS OF SPECIFICATION 16727 (DATA CABLING SYSTEM). THE DIVISION 16 ELECTRICAL CONTRACTOR SHALL TERMINATE CAT 6 WIRING TO PATCH PANEL IN BACNET DATA CABINET IN MAIN TELECOMMUNICATIONS ROOM AND IN BACNET WALL DATA ENCLOSURES IN EACH INTERMEDIATE TELECOMMUNICATION CLOSET LOCATED CENTRALLY AND STACKED ON EACH FLOOR.

*Qty (1) BACnet Data Cabinet

        - Furnish and Install UPS

        - Furnish and Install (Rack Mounted) BACnet Server

        - Furnish and Install LCD Display

          - Keyboard

          - Mouse

        - Install Cisco 24 Port Switch (Switch Furnished by Others)

*24 PORT PATCH PANEL BY OTHERS

*ENCLOSURE BY OTHERS

Qty (5) Multiple BACnet Router Data Cabinet

        - Furnish NEMA 12K Enclosure – (Qty. 5 Total) Installation by Others

        - Furnish and Install BACnet IP Router – (Qty. 7 Total)

        - Furnish and Install 7AMP Circuit Breaker – (Qty. 5 Total)

        - Furnish and Install Control Transformer – (Qty. 5 Total)

Qty (4) Power Distribution Panel LVCP-1, 2, 4, 5

        - Furnish 24V Power Distribution Panel for Installation by Others

          - Transformer w/ Circuit Breaker

          - Enclosure

        - Furnish and Install 7AMP Circuit Breaker

*ASSUMED AS PER STANDARD PRACTICE

Qty (1) Global Points

        - Furnish and Install Outside Air Temperature

        - Furnish and Install Outside Air Humidity

        - Furnish and Install Outside Air CO2

Qty (4) Packaged Air Handling Unit AHU-1, 2, 3, 4

        - Install and wire Space Temperature / Humidity Sensor (Furnished by Unit Mfr.)

        - Install and wire Duct Static Pressure Sensor (Furnished by Unit Mfr.)

        - Tie-in Fire Alarm Shutdown Signal from Fire Alarm Control Panel

        - Furnish BMS Communication Wiring to Factory Controls – (Qty. 4 Total)

        - Map Available Points Via Mfr. Provided BMS Interface

- AME Requires Mfr. Rep to Assist in Integration, cost to be Incurred by Mech Contractor

        - Furnish BMS Communication Wiring to VFD Factory Controls – (Qty. 8 Total)

        - Map Available Points Via Mfr. Provided BMS Interface

- AME Requires Mfr. Rep to Assist in Integration, cost to be Incurred by Mech Contractor

        - Furnish BMS Communication Wiring to Enthalpy Wheel VFD Controls – (Qty. 4 Total)

        - Map Available Points Via Mfr. Provided BMS Interface

- AME Requires Mfr. Rep to Assist in Integration, cost to be Incurred by Mech Contractor

*AFMS, A2L REFRIGERANT LEAK DETECTION SYSTEM BY UNIT MFR.

Qty (1) Packaged Air Handling Unit AHU-5

        - Install and wire Space Temperature / Humidity / CO2 Sensor (Furnished by Unit Mfr.)

        - Tie-in Fire Alarm Shutdown Signal from Fire Alarm Control Panel

        - Furnish BMS Communication Wiring to Factory Controls

        - Map Available Points Via Mfr. Provided BMS Interface

- AME Requires Mfr. Rep to Assist in Integration, cost to be Incurred by Mech Contractor

        - Furnish BMS Communication Wiring to VFD Factory Controls – (Qty. 2 Total)

        - Map Available Points Via Mfr. Provided BMS Interface

- AME Requires Mfr. Rep to Assist in Integration, cost to be Incurred by Mech Contractor

        - Furnish BMS Communication Wiring to Enthalpy Wheel VFD Controls

        - Map Available Points Via Mfr. Provided BMS Interface

- AME Requires Mfr. Rep to Assist in Integration, cost to be Incurred by Mech Contractor

*AFMS, A2L REFRIGERANT LEAK DETECTION SYSTEM BY UNIT MFR.

Qty (1) Packaged Air Handling Unit AHU-6

        - Install and wire Space Temperature / Humidity / CO2 Sensor (Furnished by Unit Mfr.)

        - Tie-in Fire Alarm Shutdown Signal from Fire Alarm Control Panel

        - Furnish BMS Communication Wiring to Factory Controls

        - Map Available Points Via Mfr. Provided BMS Interface

- AME Requires Mfr. Rep to Assist in Integration, cost to be Incurred by Mech Contractor

        - Furnish BMS Communication Wiring to VFD Factory Controls – (Qty. 2 Total)

        - Map Available Points Via Mfr. Provided BMS Interface

- AME Requires Mfr. Rep to Assist in Integration, cost to be Incurred by Mech Contractor

*AFMS, A2L REFRIGERANT LEAK DETECTION SYSTEM BY UNIT MFR.

Qty (58) Variable Air Volume Box – VAV

        - Furnish DDC Controller to the Factory for Installation

        - Furnish and Install Space Temperature / CO2 Sensor

        - 24V Transformer by Unit Mfr.

Qty (19) Constant Air Volume Box CAV-## (NO CONTROL INFORMATION PROVIDED)

        - Furnish DDC Controller to the Factory for Installation

        - 24V Transformer by Unit Mfr.

Qty (4) Fan Powered Variable Air Volume Box w/ Heating Coil – FPVAV

        - Furnish DDC Controller to the Factory for Installation

        - Furnish and Install Space Temperature / CO2 Sensor

        - Furnish Fan Start / Stop and Status

        - Furnish and Install Discharge Air Temperature Sensor

        - Furnish Electric Heat SCR Control

        - 24V Transformer by Unit Mfr.

Qty (10) Split System Indoor Unit AC-## | Qty (10) Outdoor Unit ACCU-##

        - Install and wire Programmable Thermostat (Furnished by Unit Mfr.)

        - Furnish and Install Space Temperature / Humidity Sensor (BMS Monitoring)

        - Furnish and Install Leak Sensor

        - Tie-in Condensate Pump Float Switch (Furnished by Mfr.) – As per Detail 5 (M504)

        - Low Voltage Interlock Wiring between Indoor and Outdoor Unit

        - Furnish BMS Communication Wiring to Factory Controls

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

Qty (1) Split System Indoor Unit AC-502 | Qty (1) Outdoor Unit ACCU-502

Qty (1) Energy Recovery Ventilator Unit ERV-502

Qty (2) Gravity Ventilator GV-502-IN, EX

Qty (1) Electric Duct Heater EDH-502

        - Install and wire Programmable Thermostat (Furnished by Unit Mfr.) (For Split System)

        - Furnish and Install Space Temperature / Humidity Sensor (BMS Monitoring)

        - Furnish and Install Gravity Ventilator Damper Actuator – (Qty. 2 Total)

        - Furnish and Install Leak Sensor

        - Tie-in Condensate Pump Float Switch (Furnished by Mfr.) – As per Detail 5 (M504)

        - Necessary Low Voltage Interlock Wiring between ERV Unit and Split Indoor Unit Operation

        - Necessary Low Voltage Interlock Wiring between EDH and Split Indoor Unit Operation

        - Necessary Low Voltage Control Wiring between ERV Unit Factory Relay Module for Damper Control and Split Indoor Unit

        - Low Voltage Interlock Wiring between Split Indoor and Outdoor Unit

        - Furnish BMS Communication Wiring to Split Factory Controls

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

        - Furnish BMS Communication Wiring to Energy Recovery Ventilator Factory Controls

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

Qty (3) Toilet Exhaust Fan TEF-1, 2, 3

        - Furnish and Install DDC Controller

        - Furnish Fan Start / Stop and Status

        - Furnish and Install Exhaust Fan Damper Actuator – (Qty. 3 Total)

Qty (1) Electric Room Exhaust Fan EF-1

        - Furnish and Install DDC Controller

        - Furnish and Install Space Temperature Sensor

        - Furnish Fan Start / Stop and Status

        - Furnish and Install Exhaust Fan Damper Actuator

Qty (1) Shower Room Exhaust Fan EF-2

Qty (2) Storage Room Exhaust Fan EF-3, 8

Qty (1) Water Service Room Exhaust Fan EF-5

Qty (2) Locker Room Exhaust Fan EF-6, 10

        - Furnish and Install DDC Controller

        - Furnish Fan Start / Stop and Status

        - Furnish and Install Exhaust Fan Damper Actuator – (Qty. 6 Total)

Qty (1) Art Storage Room Kiln Exhaust Fan EF-7

        - Interlock Wiring with Associated Unit Operation

        - Furnish and Install CT for Fan Status; Connect to Nearby DDC

        - Furnish and Install Damper Actuator

*Qty (1) Can Wash Kitchen Exhaust Fan EF-9 (SEE AME ADD ALT)

        - Connect to Nearby DDC

        - Furnish and Install CT for Fan Status

        - Furnish and Install Damper Actuator

*CONTINUOUS OPERATION – AS PER CONTROL DIAGRAM (M412.00)

Qty (1) MEP Storage Room Exhaust Fan EF-11 | Qty (1) Motorized Damper MD-2

        - Furnish and Install DDC Controller

        - Furnish Fan Start / Stop and Status

        - Furnish and Install Exhaust Fan Damper Actuator

        - Furnish and Install Make-up Air Damper Actuator

Qty (3) Post-Fire Smoke Purge Fans SPF-1, 2A, B | Qty (1) Motorized Damper MD-1

        - Furnish and Install Damper Actuator – (Qty. 4 Total)

- *FANS ARE CONTROLLED VIA SMOKE PURGE PANEL FIRE ALARM SYSTEM

Qty (1) General Kitchen Exhaust Fan KEF-1

        - Furnish and Install DDC Controller

        - Furnish and Install Space Temperature Sensor

        - Furnish Fan Start / Stop and Status

        - Furnish and Install Damper Actuator

- *AS PER CONTROL DIAGRAM (M412.00)

- Kitchen Exhaust System

Qty (1) Kitchen Exhaust Fan KEF-2

Qty (2) Kitchen Hood

        - Interlock wiring b/w AHU and Kitchen Exhaust Fan Operation

        - Interlock wiring w/ Dietician’s HOA Switch at Kitchen Hood Control Panel Operation

        - Furnish and Install CT for Fan Status

        - Furnish and Install Damper Actuator (Exhaust Fan)

Qty (1) Canopy Area Supply Fan SF-100B | Qty (1) Electric Duct Heater EDH-1

        - Furnish and Install DDC Controller

        - Furnish and Install Space Temperature Sensor

        - Furnish Supply Fan Start / Stop and Status

        - Furnish EDH Enable / Disable, Status

        - Furnish and Install EDH Discharge Air Temperature Sensor

Qty (1) Roof Storage Room Exhaust Fan EX-R03 | Qty (2) Motorized Damper MD-3, 4

        - Furnish and Install DDC Controller

        - Furnish Fan Start / Stop and Status

        - Furnish and Install Exhaust Fan Damper Actuator

        - Furnish and Install Make-up Air Damper Actuator

Qty (2) Electric Air Curtain ARC-1.1, 1.2

        - Interlock w/ Door Switch (Furnished by Unit Mfr.) – (Qty. 4 Total) 2 per Unit (As per Schedule)

- *INTEGRAL THERMOSTAT

Qty (4) Recessed Wall Electric Cabinet Unit Heater CBH-A

        - Furnish and Install BACnet Thermostat – (Qty. 1 Total)

Qty (43) Electric Cabinet Unit Heater ECUH-##

        - Furnish and Install BACnet Thermostat – (Qty. 42 Total)

Qty (11) Electric Unit Heater EUH-##

        - Furnish and Install BACnet Thermostat – (Qty. 11 Total)

Qty (105) Electric Baseboard Heater

        - Interlock with Associated VAV Unit Operation

Qty (8) Electric Baseboard Heater

        - Furnish and Install BACnet Thermostat – (Qty. 5 Total)

*Qty (3) Heat Pump Water Heater HPWH-1, 2, 3 | Qty (2) Recirculating Pump HWCP-1, 2 – As per Control Diagram 1 (M413.00)

        - Furnish and Install DDC Controller

        - Furnish and Install Hot Water Supply / Return Temperature Sensor – (Qty. 4 Total)

        - Furnish and Install CT for Recirculating Pump Status – (Qty. 2 Total)

        - Electrical Power Meter (Furnished and Installed by Others) – (Qty. 3 Total)

          - BMS Communication Wiring to Mfr. Provided BMS Interface

        - Furnish BMS Communication Wiring to HWHP Factory Controls – (Qty. 3 Total)

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

        - Furnish BMS Communication Wiring Domestic HW Control Panel Controls – As per Note 2 (M413)

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

- *MIXING VALVE BY OTHERS

Qty (1) Emergency Generator

        - Furnish Control Wiring b/w Generator and Remote-control Panel

        - Furnish Belly Fuel Tank Alarm Via Common Alarm Output

          - High Level Alarm

          - Low Level Alarm

          - Leak Alarm

        - Furnish and Install Horn and Strobe Sensor – As per 15985 - 86

        - Furnish and Install Damper Actuator – As per 15985 - 91

        - Furnish BMS Communication Wiring to Generator Factory Controls

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

        - Furnish BMS Communication Wiring to Alarm Panel

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

- *Remote Annunciator Panel in the Custodian’s Office by Others

Qty (2) Sub-Slab Depressurization System SF-1, 2 (H205.00)

        - Furnish and Install Interposing relay for Mfr. Provided DP Switch for BMS Connection – As per H205.00

        - Furnish BMS Communication Wiring to Factory Controls

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. rep to assist in integration, cost to be incurred by Mech Contractor

Qty (1) Refrigerant Shaft Leak Detection – As per Keynote 7 (M101.00)

        - Furnish and Install Refrigerant Leak Detection Sensor

        - Furnish and Install Damper Actuator

        - Necessary Interlock Wiring with Fire Alarm System

Misc Monitoring Systems

        - Map Available Points Via Mfr. Provided BMS Interface or Connect to Nearby DDC Controller

        - Main Electrical Meter (Furnished and Installed by Others) – (Qty. 1 Total)

            - Mfr. to Provide Pulse Output for Monitoring at BMS

        - Utility Electrical Meter (Furnished and Installed by Others) – (Qty. 2 Total)

            - Mfr. to Provide Pulse Output for Monitoring at BMS

        - Main Switchboard Meter (Furnished and Installed by Others) – (Qty. 2 Total)

            - Mfr. to Provide Pulse Output for Monitoring at BMS

        - Panel Electric meter for Below Mentioned Panels (Furnished and Installed by Others) – (Qty. 43 Total)

              - PP-## – (Qty. 16 Total)

              - ELP-## – (Qty. 7 Total)

              - EPP-## – (Qty. 6 Total)

              - LP-## – (Qty. 6 Total)

              - RP-## – (Qty. 6 Total)

              - DIM-AUD – (Qty. 1 Total)

              - DB-ELEV – (Qty. 1 Total)

            - BMS Communication Wiring to Mfr. Provided BMS Interface

        - Electric meter for Feeder Serving Each Roof top Unit (Furnished and Installed by Others) – (Qty. 6 Total) As per Energy Metering Detail (M407.00)

        - Electric meter for Air Cooled Condensing Unit (Furnished and Installed by Others) – (Qty. 11 Total) As per Energy Metering Detail (M407.00)

        - Elevator Sump Pump EVP-1 (Qty. 1 Total)

            - Pump Status

            - High Level Alarm

        - Domestic Water Incoming Water Filter F1 (Qty. 1 Total)

            - Head of Serv Common Alarm

            - Head of Serv Backwash Status

        - Domestic Water Booster Pump Panel WBP-1 (Qty. 1 Total)

            - Booster Pump Set General Fault Alarm

            - Tie-in Mfr. Provided Watt Meter into BMS via Mfr. Provided BACnet Interface

            - Furnish BMS Communication Wiring to VFD Factory Controls – As per Note 5 (M407.00)

            - Map Available Points Via Mfr. Provided BMS Interface

              - AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

        - Intrusion Alarm

Provide 2 Year Full Preventive Maintenance contract including all labor, materials and equipment necessary for the successful operation of the entire BACnet BMS/DDC Temperature Control System as provided by the TCC – 15970-42

Guarantee / Warranty

        - 2 Year Workmanship and Material Guarantee for all work of this Section starting from completion of the commissioning of the system. – As per 15970-40

        - Provide a 4-year manufacturer’s warranty for the Supervisor Station, SOC, and POT. – As per 15970-41

        - Provide a 5-year software subscription service for the application software for the Tridium Supervisor Server. – As per 15970-30

Provide 2 Year Guarantee for Workmanship and Material – 15970-49

- ADD ALTERNATES:

- ALT 1: Controls As per Sequence of operation 15985 – 18

*Qty (1) Can Wash Kitchen Exhaust Fan EF-9

        - Furnish and Install DDC Controller

        - Furnish Fan Start / Stop and Status

- DEDUCT ALTERNATES:

- ALT #:

Qty (1) Shower Room Exhaust Fan EF-2

        - Furnish and Install CT for Fan Status; Connect to Nearby DDC

        - Furnish and Install Damper Actuator

*CONTROLLED THROUGH LOCAL MANUAL SWITCH – AS PER SEQUENCE OF OPERATION (15985 – 18)

Clarifications and Inclusions considered:

All labor will be performed during normal business working hours (M to F, 7AM to 4PM).

All Motor starters require Hand-Off-Auto switches, control transformers and coils.

All Motor starters and/or variable frequency drive are to be located within the vicinity of the associated controlled equipment.

The Division 23 BMS electrical work shall be performed in accordance with the following installation practices:

All new wiring in exposed or wiring in machine equipment rooms shall be in EMT conduit.

All new wiring in exterior areas, or where exposed to the elements shall be installed with galvanized EMT or RGS conduit with appropriate fittings.

All unexposed low voltage wiring outside of the mechanical equipment rooms, where applicable, can be in plenum rated cable.

The fire stopping of the new BMS control wiring is included.

The Division 26 EC shall deliver a designated power source to within 5 feet of BMS control panels.

Exceptions and Exclusions: The following items, unless specifically mentioned in the “Scope of Work and Equipment included” or the “Clarifications” sections of this document are excluded from this quotation.

All off-hours or overtime labor.

All temporary heating or cooling.

All equipment manufacturer integration/communication devices, setup and/or programming.

All equipment manufacturer wall sensor guards, if required.

The integration and communications into competitive building management systems.

The cost of material & setup of the third party communication devices.

All water flow and/or air flow balancing and calibration.

The installation of dampers, valves, wells, water flow meters and/or air flow stations.

The installation of control valves, piping taps and thread-o-lets.

All power wiring of mechanical equipment (RTU, VFD, Pumps, Boiler, UH, UV, FCU, etc.).

EMT or RGS conduit (if specified) other than exterior areas and mechanical equipment rooms.

Any computers and/or related equipment, including but not limited to, routers, monitors, printers, etc.

All mechanical equipment (i.e. AHU, VAV, Pumps, VFDs, etc.).

All air flow monitoring station.

All water flow meters.

All electric power meters.

All gas meters.

All motor starters.

All variable frequency drives.

Any equipment housekeeping pads

The Boiler Control Panel and associated control devices.

Any gas detection system or components.

Any demolition work not mentioned.

All fire alarm system or components, smoke, combination fire/smoke dampers, smoke detectors and associated wiring.

Installation and maintenance of any high-speed internet connections.

All control dampers.

Any site excavation and/or trenching.

All cutting, patching, and/or painting.

Any core drilling of floors, walls and/or partitions.

Any roof penetrations, pitch pockets required.

Any costs associated for factory-mounting and wiring of AME provided devices.

All site cleanup back-up charges not produced by the work under this Scope of Work.

Any checkout, repair, replacement, or warranty of existing controlled equipment.

Any bid, performance, maintenance, or payment bonds.

Any Taxes and/or Permit Fees (on applicable jobs)

All project allowances

Any demolition work not specifically mentioned

EXCEPTION TO ANY WORK WITH EXHAUST FAN EF-4 (24/7 OPERATION)

Base Price: ……………………$

This price is valid for 30 days from the quoted date

Pricing is subject to change based on tariffs

ADD ALTERNATE:

- ALT # - ……………………$

DEDUCT ALTERNATE:

- ALT # - ……………………$

Thank you for the opportunity to quote this job. Should you have any questions, please feel free to call me direct.

Respectfully,

# Eric Niedle

# Eric Niedle

# A.M.E., Inc.

# Connected Buildings Made Smarter

Corporate Headquarters 
695 US-46 Suite 403, Fairfield, NJ 07004

AME New York

Long Island City, NY 11101

GENERAL CONTACT

973-884-4100

info@ame-inc.com

www.ame-inc.com

AME Pennsylvania 
Newtown, PA 18940

SERVICE AND SUPPORT

973-884-4100

service@ame-inc.com

Support Hours: 24/7/365

AME Texas 
Dallas, TX