# Estimation Guidelines

Scope of Work Format

Qty (#) System Header

        - Scope line items

        - Furnish and Install ABC (Qty. ## Total) (Detailing information)

        - Furnish and Install ABC (as per sequence)

        - Furnish and Install ABC (Location: 3rd Floor)

        - Furnish ABC

        - Furnish and Wire ABC

        - Install and Wire ABC (Furnished by Unit Mfr.)

        - Install ABC (Furnished by Unit Mfr.)

        - Wire ABC (Furnished by Unit Mfr.)

- **Clarification

- **Start/Stop via Fire Alarm System

- **Refrigeration Leak Detection system is coming with the unit per equipment schedule

# Integration Lines that go together (all 3) samples

        - Furnish BMS Communication Wiring to Factory Controls

        - Map Available Points Via Mfr. Provided BMS Interface

          - AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

        - Furnish BMS Communication Wiring to Chiller Factory Controls

        - Map Available Points Via Mfr. Provided BMS Interface

          - AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

        - Furnish BMS Communication Wiring to VFD Controls

        - Map Available Points Via Mfr. Provided BMS Interface

          - AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

How to use this template and read this:

          - This is for guidance not bible.

How a system is presented can be referred here.

All points under the scope are written per available control information. In no case this is a mandatory point list. In real jobs these points will change per that specific jobs available control information

# Front End Template:

What is this?
→ This is a how we write a Front-end Scope. Two Variations New and Extension of Existing BMS

→ Most of the information is found in specs section 230900 and similar, Name of the Sections are Instrumentation and HVAC, Direct Digital Control (DDC) System for HVAC etc.

→(these are additional insights for you, do not print them in scope of work)

# New:
A.M.E., Inc, is pleased to provide a quotation on the above project to provide Automated Temperature Controls system.

#### SCOPE OF WORK –

- Front End Web Enabled BMS System

  - Furnish Network Level Control Panel

    - (This is Centralized Building Level Controller, Honeywell WEBS, Johnson FX etc. Often Mentioned in the Specs)

  - Furnish PC Workstation

    - (Mentioned in Specs)

  - Furnish BMS Server

    - (Mentioned in Specs)

  - Furnish POT (Laptop or Tablet)

    - (Mentioned in Specs)

  - Furnish UPS – For workstation, server, network level control panel

    - (Mentioned in Specs)

  - Furnish 3-D Graphics

    - Default

  - Furnish Necessary Training on New Controls

    - Default

  - IT Infrastructure – By AME or by Others? (mentioned in specs, applicable if protocol is BACnet/IP)

    - Network Switches

    - Panels

    - Fiber – Ethernet

## OR

## Extension of Existing :

## →IF AME already has a BMS in the building, we would generally provide the new network level control panel, and utilize existing BMS architecture to save the cost

## A.M.E., Inc, is pleased to provide a quotation on the above project to provide an extension of the existing District Wide BMS system.

#### SCOPE OF WORK –

- Seamlessly Tie in to the Existing Honeywell / Niagara N4 BMS

  - Furnish Network Level Control Panel

  - Furnish 3-D Graphics to match existing

  - Furnish Necessary Training on New Controls

Warranty scope of work- (mentioned in specs)

- a one-year preventative maintenance service contract covering all parts, materials, software, hardware, and all costs to provide software and hardware upgrades during the warranty period. (mentioned in specs)

- extend the maintenance service contract and the warranty for four additional years following the warranty period.  (mentioned in specs)

Qty (1) Existing Fan Coil Unit, FCU (when unit and stat both getting relocated)

        - Demo and safe-off existing control wiring prior to relocation of unit

        - Extend control wiring for relocated existing thermostat

        - Furnish and Install Damper Actuator

        - Extend communication bus to new unit location

        - Re-commission unit to ensure proper operation

Qty (#) Fire / Smoke Dampers FSD

        - Necessary Low Voltage Interlock Wiring

        - Furnish Open / Close Status to BMS via FSD End Switch (End switch provided w damper by others)

- OR

        - Low Voltage Interlock with Associated Unit Fan Starter

- **tech hour: 0.5 hour each qty

Qty (#) Apartment Heat Pumps HP-A Thru I

        - Install and Wire Programmable Thermostat (Furnished by Unit Mfr.)

          - This is often declared under schedule or sequence of operation

        - Furnish and Install Leak Sensor

        - Furnish and Install Nest Thermostat ( Alternate) check schedule for notes)

- *Apartment heat pumps are usually seen on the high riser buildings

- *Qty range is around 100s to 1000s.

- *Often Qty. multiply due to typical floor layout in mechanical plans

- **tech hour: 0.3 hour each qty

Qty (#) HVAC Alarm Panel w/ Auto Dialer

        - Furnish and Install Sensaphone

        - Monitor the following Alarms

  - High / Low Room Temperature/Humidity **** Unit

  - Leak Detection at **** Unit

  - Common Alarms at *****AC Unit

          - EXCEPTION TO AUTO DIALER (BMS CAN SEND OUT ALARMS VIA EMAIL AND SMS TEXT)

- *Sensaphone – A device that AME will use in lieu of Network Level Control Panel to send of email notification for Alarms, often used on small jobs with Standalone Setting.

- (Sensaphone or Similar word is used in the specs / sequence 99% of the time)

- **tech hour: 8 hour each qty

Qty (1) Stair / Elevator Vent -

        - Furnish and Install Damper Actuator (Smoke Detector by Others)

- *This is mentioned on the plans and air riser, a damper actuator symbol with arrow and a note nearby mentioned damper actuator in the stair controlled by smoke detector, then we use above scope

- **tech hour: 1 hour each qty

Qty (2) VAV / Fan VAV Master Template

        - Furnish DDC Controller to the Factory for Installation

        - Furnish and Install Space Temperature Sensor; applicable

- OR

        - Furnish and Install Space Temperature / Humidity Sensor

- OR

        - Furnish and Install Space Temperature / Humidity / CO2 Sensor

- OR

        - Furnish and Install Space Temperature / CO2 Sensor

        - Furnish Fan Enable; Only applicable when Fan powered VAV is mentioned in the schedule

        - Furnish and Install Discharge Air Temperature Sensor; mandatory when we have reheat VAV; meaning there is heating coil mentioned in the schedule

        - Furnish and Wire Hot Water Control Valve and Actuator

        - OR

        - Furnish Electric Heat Enable (DO)

- OR

        - Furnish Electric Heat SCR Control (AO)

        - Run 24V Power Loop to VAVs (Mentioned 24 V Wiring Control by BMS Contractor)

- OR

- Furnish and Install VAV Transformer;

- OR

        - 24V VAV Transformer is Coming with the Unit

- **Above VAV template takes care all VAV configuration, selecting required lines per sequence of operation

- ** T, T/H, T/H/CO2, T/CO2 information is mostly in the sequence, sensor location can be on the plans

- **Cooling only VAV – only needs T, T/H, T/H/CO2, T/CO2 (one as declared in the sequence)

- **Reheat VAV – Hot water; we include hot water control valve and actuator. Look for GPM in VAV schedule

- **Reheat VAV – Electric SCR; Look for SCR in schedule / sequence

- **Reheat VAV – Electric Heat; Look for kW in schedule / sequence

- **tech hour: 4 hour each for each hot water reheat VAV

- **tech hour: 3 hour each for each cooling only VAV

Qty (#) Finned Tube Radiation FTR – Hot water

        - Furnish and Wire Hot Water Control Valve and Actuator

        - Interlock with Associate VAV / FCU/ System Operation

- **tech hour: 1 hour each FTR

Qty (#) Finned Tube Radiation FTR – Electric

        - Interlock with Associate VAV / FCU/ System Operation

- **FTR / perimeter similar names are used and they are seen sharing a space with primary equipment VAV, FCU, RTU, Split System etc

- **tech hour: 1 hour each FTR

Qty (#) Exhaust Fans EF-#

        - Interlock with Associated AHU / RTU /MAU Unit Operation

        - Furnish and Install Damper Actuator

- **When sequence mentions Exhaust fan operation shall be interlocked with Associated unit, we can use something like this,

- Gas Detection Panel (Garage/ Parking / Loading Dock system) Stand Alone Operation

Qty (#) Gas Detection Panel

Qty (#) Exhaust Fan

Qty (#) Supply Fan

        - Furnish and Install Gas Detection Panel (Qty. ##)

          - CO/NO2 Sensor (Qty. ##)

          - Remote Horn / Strobe Sensor (Qty. ##)

        - Interlock Fan Operation with Gas Detection Panel

        - Furnish and Install Damper Actuator

        - Tie into BMS

- **Gas Detection panel is the most important and expensive system, cant miss panel and sensor qty.
** Sensors are shown on the plans mostly

- **Gas detection type: CO/NO2 (parking / loading dock / Garage)

- **Gas detection type: H2 Hydrogen (Battery room, UPS Room)

- **Gas detection type: O2 Oxygen

- **Gas detection type: CO/CH4 (at boiler)

- **Gas detection type: refrigeration (at chillers)

- ** We always source quotes for this

- **tech hour: 4 hour each fan

- **tech hour: 8 hour each gas panel

Qty (3) Toilet Exhaust Fan TX-1 thru 3

        - Furnish and Install Timeclock

        - Furnish and Install Damper Actuator w/ End Switch

- **tech hour: 2 hour each fan

- **Timeclock device often used when we have a standalone system

Qty (#) Exhaust Fan EF-

        - Furnish and Install DDC Controller

        - Furnish and Install Space Temperature Sensor

        - Furnish and Install Duct Static Pressure Sensor

        - Furnish Fan Start / Stop and Status

        - Furnish Fan VFD Control

        - Furnish and Install Damper Actuator w/ End Switch

- **tech hour: 4 hour each fan if gets more points.

Kitchen Exhaust Ventilation

Qty (#) Kitchen Exhaust System KEF-1

Qty (#) Dishwashing DWEF-1 |

Qty (#) Makeup Air Unit MAU-1 |

Qty (#) Pollution Control Unit PCU-1

        - Install and Wire Space Temperature Sensor (Furnished by Unit Mfr.)

        - Interlock wiring b/w MAU and Kitchen Exhaust Operation

        - Low Voltage Control Interlock w/ Kitchen Hood Operation

        - Furnish and Install Damper Actuator (Exhaust Fan)

- **tech hour: 40 hour each

- **this is a complex system; most heavy lifting is done here by kitchen equipment contractor and we are responsible for doing interlocks of the kitchen hood control panel with the makeup system and the kitchen hood exhaust fan so that all of the system works in coordination. We don't have to provide kitchen hood control panels. This is complex. It is done by the special contractor, and our scope is limited to the interlock wiring between the kitchen hood control panel, kitchen hood, dishwasher, makeup air, and the kitchen hood exhaust, as applicable.

- Dryer Exhaust Fans DX

Qty (1) Laundry / Dryer Exhaust Fan DX-#-#

        - Interlock wiring to Differential Pressure Controller (Furnished by Unit Mfr.)

        - Furnish and Install Damper Actuator

        - Furnish BMS Communication Wiring to Factory Controls

        - Map Available Points Via Mfr. Provided BMS Interface

          - AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

- **tech hour: 4 hour each

- **Fan Comes with the Pressure Controller, we have to interlock fan with pressure controller

Qty (2) Post-Fire Smoke Purge Fans SX-44-1 & 2 | Pool Post Fire Smoke Purge EF-4-1

        - Furnish and Install Fan Status

        - Furnish and Install Damper Actuator

- *Fans Are Controlled via Fire Alarm System

Qty (1) Packaged ERU / RTU / AHU

        - Install and wire Space Thermostat (Furnished by Unit Mfr.)

        - Install and wire Supply Air Temperature Sensor (Furnished by Unit Mfr.)

        - Install and wire Duct Static Pressure Sensor (Furnished by Unit Mfr.)

        - Install and wire mfr. Provided sensors shipped loose w/ unit; if info not available about particular shipped loose end devices

        - Furnish BMS Communication Wiring to Factory Controls

        - Map Available Points Via Mfr. Provided BMS Interface

- AME Requires Mfr. Rep to Assist in Integration, cost to be Incurred by Mech Contractor

- **Here unit manufacturer is providing a DDC Controller and we are going to integrate it into Our BMS. Along with that OEM will ship loose few end devices that we need to install and wire

- *schedule notes and sequence often clears who is providing the controls

Qty (2) Fan Coil Unit FCU

        - Furnish and Install DDC Controller

        - Furnish and Install Space Temperature Sensor

        - Furnish and Install Discharge Temperature Sensor

        - Furnish Fan Start / Stop (low, med, hi) and Status

        - Furnish and Wire Filter DP Switch

        - Furnish and Wire Cooling Coil Control Valve and Actuator

        - Furnish and Wire Heating Coil Control Valve and Actuator

        - Furnish and Install Leak Sensor

        - Furnish and Install Damper Actuator

- **tech hour: 4 hour per fcu

Qty (##) Air handling Unit AHU

        - Furnish and Install DDC Controller

        - Furnish and Install Supply Static Pressure Sensor

        - Furnish and Install Building Static Pressure Sensor

        - Furnish and Install Chilled Water Coil Supply/Return Temperature Sensor

        - Furnish and Install Hot Water Coil Supply/Return Air Temperature Sensor

        - Furnish and Install Coil Leaving Air Temperature Sensor

        - Furnish and Install Space Temperature / Humidity Sensor

        - Furnish and Install Discharge Air Temperature Sensor

        - Furnish and Install Discharge Air Humidity Sensor

        - Furnish and Install Mixed Air Temperature Sensor

        - Furnish and Install Return Air Temperature Sensor

        - Furnish and Install Return Air Humidity Sensor

        - Furnish and Install Return Air CO2 Sensor

        - Furnish Supply Fan Start/Stop and Status

        - Furnish Supply Fan VFD control

        - Wire Supply Fan Flow Transmitter (Furnished by Others)

        - Furnish and Install DP Sensor for Supply Airflow Monitoring (Piezo Ring)

        - Furnish Exhaust Fan Start/Stop and Status

        - Furnish Exhaust Fan VFD control

        - Wire Exhaust Fan Flow Transmitter (Furnished by Others)

        - Furnish and Install DP Sensor for Exhaust Airflow Monitoring (Piezo Ring)

        - Furnish Heat Wheel Start/Stop and Status

        - Furnish Heat Wheel VFD Control

        - Furnish Freeze Protection Pump Start/Stop and Status

        - Furnish and Install High Static Pressure Switch

        - Furnish and Install Low Suction Pressure Switch

        - Furnish and Install Freezestat

        - Furnish and Wire Filter DP Switch

        - Furnish and Wire Outside Air Flow Measuring Station

        - Furnish and Wire Supply Air Flow Measuring Station

        - Furnish and Install Outside Air Damper Actuator

        - Furnish and Install Exhaust Air Damper Actuator

        - Furnish and Install Return Air Damper Actuator

        - Furnish and Install Heat Wheel Face/Bypass Air Damper Actuator (Qty. 2)

        - Furnish and Wire Hot Water Control Valve and Actuator

        - Furnish Electric/Gas Heat Enable

        - Furnish and Wire Cooling Coil Water Control Valve and Actuator

        - Furnish DX Cooling Enable / Disable

        - Furnish Humidifier Enable / Disable

        - Furnish Humidifier Control Valve and Actuator

        - Furnish and Install High Limit Humidity Switch

        - Furnish and Install Leak Sensor

- (**tech hour: 2 hour each hardware point)

Qty (1) Heat Exchanger System HX-2 | HWP-1, 2

        - Furnish and Install DDC Controller

        - Furnish and Install Outside Air Temperature / Humidity Sensor

        - Furnish and Install System ### Water Supply / Return Temperature Sensor

        - Furnish and Install Building ### Water Supply / Return Temperature Sensor

        - Furnish and Install HX Supply /Return Water Temperature Sensor

        - Furnish Pump Start/ Stop and Status

        - Furnish Pump VFD Control

        - Furnish and Install Differential Pressure Transmitter

        - Furnish and Install Hot Water Flow Meter

        - Furnish and Install Steam Flow Meter

        - Furnish and Install BTU Meter – Flow Meter, Supply / Return Temperature Sensor

        - Furnish and Wire ##” HX Steam Control Valve and Actuator (1/3rd-2/3rd)

        - Furnish and Wire ##” HX Primary Control Valve and Actuator

        - Furnish and Wire ##” HX Secondary Control Valve and Actuator

        - Furnish and Wire ##” Differential Pressure Bypass Control Valve and Actuator

- (**tech hour: 2 hour each hardware point)

Qty (1) Heat Exchanger System HX-1 | Pump-1, 2

        - Furnish and Install DDC Controller

        - Furnish and Install System ### Water Supply / Return Temperature Sensor

        - Furnish and Install Building ### Water Supply / Return Temperature Sensor

        - Furnish and Install HX Supply /Return Water Temperature Sensor

        - Furnish Pump Start/ Stop and Status

        - Furnish Pump VFD Control

        - Furnish and Install Differential Pressure Transmitter

        - Furnish and Install Chilled Water Flow Meter

        - Furnish and Install Steam Flow Meter

        - Furnish and Wire ##” Heat Exchanger Control Valve and Actuator

        - Furnish and Wire ##” Differential Pressure Bypass Control Valve and Actuator

- (**tech hour: 2 hour each hardware point)

          - Chilled Water System

- Qty (2) ACCH-5R-1, 2

- Qty (3) Chilled Water Glycol Pump CHGP-5-1, 2, 3

- Qty (1) Expansion Tank ET-5-1

        - Furnish and Install DDC Controller (Qty. 1)

        - Furnish and Install UPS for DDC Controller (As per Controls 5/M-818)

        - Furnish and Install Chiller Chilled Glycol Temperature Transmitters (TT-01 thru 04) (Qty. 4 Total)

        - Furnish and Install Main BTU Meter - Flow Meter, Temperature Transmitter (BTU01, FT-01, TT-05, 06) (Qty. 1)

        - Furnish and Install Chiller Differential Pressure Transmitters (DP-01, DP-02) (Qty. 2 Total)

        - Furnish and Install System Differential Pressure Transmitters (Roof - DPT-01) (Qty. 1 Total)

        - Furnish and Install Expansion Tank Pressure Transmitters (PT-01) (Qty. 1 Total)

        - Furnish and Install Chiller Flow Switches (FS-01, FS-02) (Qty. 2 Total)

        - Furnish Air-Cooled Chiller Enable (Qty. 2 Total)

        - Furnish Air-Cooled Chiller Status (Qty. 2 Total)

        - Furnish Air-Cooled Chiller Common Alarm (Qty. 2 Total)

        - Furnish Chiller Chilled Water Supply Temperature Setpoint (Qty. 2 Total)

        - Furnish Pump Start/Stop and Status (Qty. 3 Total)

        - Furnish Pump VFD Control (Qty. 3 Total)

        - Furnish Pump VFD Feedback (Qty. 3 Total)

        - Furnish Pump VFD Common Alarm (Qty. 3 Total)

        - Furnish and Wire 6” Chiller Isolation Control Valves and Actuator w/ (2) End Switches (ICV-01, ICV-02) (Qty. 2 Total)

        - Furnish and Wire 4” Minimum Flow Bypass Control Valve and Actuator (BPV-01) (Qty. 1)

        - Furnish BMS Communication Wiring to Chiller Factory Controls

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

        - Furnish BMS Communication Wiring to Pump VFD Controls

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

- (**tech hour: 2 hour each hardware point)

          - Chilled Water System

- Qty (3) Geothermal Heat Pump-2-1, 2, 3

- Qty (3) Chilled Water Pump CHWP-2-1, 2, 3

- Qty (3) Glycol Water Pump GWP-2-1, 2, 3

- Qty (2) Expansion Tank ET-2-1, ET-2-2

- Qty (4) Plate Frame Heat Exchanger PFHX-2-1A, 1B; PFHX-2-2A, 2B

        - Furnish and Install DDC Controller

        - Furnish and Install UPS for DDC Controller (As per Controls 5/M-818)

        - Furnish and Install Chilled Glycol Heat Exchanger Temperature Transmitters (TT-07 thru 14) (Qty. 8 Total)

        - Furnish and Install Ground Loop Heat Exchanger Temperature Transmitters (TT-15 thru 22) (Qty. 8 Total)

        - Furnish and Install Geothermal Heat Pump Temperature Transmitters (TT-23 thru 34) (Qty. 12 Total)

        - Furnish and Install Ground Water BTU Meter - Flow Meter, Temperature Transmitters (BTU-02, FT-02, TT-35, TT-36) (Qty. 1)

        - Furnish and Install Chilled Water BTU Meter - Flow Transmitters, Temperature Transmitters (BTU-03, FT-03, TT-37, TT-38) (Qty. 1)

        - Furnish and Install Geothermal Heat Pump Differential Pressure Transmitters (DP-03 thru 08) (Qty. 6 Total)

        - Furnish and Install Chilled Glycol System Differential Pressure Transmitter (DPT-02) (Qty. 1)

        - Furnish and Install Chilled Water Riser Differential Pressure Transmitters (2nd Floor - DPT-02, 4th Floor- DPT-03, Roof - DPT-04) (Qty. 2 Total)

        - Furnish and Install Geothermal Ground Loop System Differential Pressure Transmitter (2nd Floor - DPT-05) (Qty. 1)

        - Furnish and Install Chilled Water Main Flow Meter (FT-04) (Qty. 1 Total)

        - Furnish and Install Chilled Water System Makeup Water Flow Meter (FT-05) (Qty. 1 Total)

        - Furnish and Install Expansion Tank Pressure Transmitters (PT-01, PT-02) (Qty. 1 Total)

        - Furnish and Install PFHX Flow Meter (Qty. 4 Total) – as per detail

        - Furnish and Wire Geothermal Heat Pump Flow Switches (FS-03 thru 08) (Qty. 6 Total)

        - Furnish Geothermal Heat Pump Enable (Qty. 3 Total)

        - Furnish Geothermal Common Alarm (Qty. 3 Total)

        - Furnish Geothermal Heat Pump Chilled Water Setpoint (Qty. 3 Total)

        - Furnish Geothermal Heat Pump Hot Water Setpoint (Qty. 3 Total)

        - Furnish Pump Start/Stop and Status (Qty. 6 Total)

        - Furnish Pump VFD Control (Qty. 6 Total)

        - Furnish Pump VFD Feedback (Qty. 6 Total)

        - Furnish Pump VFD Common Alarm (Qty. 6 Total)

        - Furnish and Wire 8” Heat Exchanger Isolation Control Valves and Actuators w/ (2) End Switches (ICV-03 thru ICV-06) (Qty. 4 Total)

        - Furnish and Wire 6” Geothermal Heat Pump Isolation Control Valves and Actuators w/ (2) End Switches (ICV-07, ICV-08, ICV-09) (Qty. 3 Total)

        - Furnish and Wire 8” Heat Exchanger Modulating Control Valves and Actuators (MCV-01 thru MCV-04) (Qty. 4 Total)

        - Furnish and Wire 6” Geothermal Heat Pump Modulating Control Valves and Actuators (MCV-05, MCV-06, MCV-07) (Qty. 3 Total)

        - Furnish and Wire 6” Free Cooling Flow Control Modulating Control Valves and Actuators (Duty/Standby) (Qty. 2 Total) (MCV-08, 09)

        - Furnish and Wire ##” Chilled Glycol Flow Bypass Control Valve and Actuator (Qty. 1) (BPY-02)

        - Furnish and Wire ##” Geothermal Ground Loop Flow Bypass Control Valve and Actuator (Qty. 1) (BPV-03)

        - Furnish BMS Communication Wiring to Geothermal Heat Pump Factory Controls (Qty. 3 Total)

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

        - Furnish BMS Communication Wiring to Pump VFD Controls (Qty. 6 Total)

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

- (**tech hour: 2 hour each hardware point)

          - Qty (1) Furnish and Install Refrigeration Monitoring System

        - Horn and Strobe

        - Pull Station

        - Remote Refrigeration Sensor

        - Necessary Low Voltage Control Wiring Mfr. Provided Controls

        - Furnish BMS Communication Wiring to Factory Controls

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

- (**tech hour: 8 hour per panel)

Qty (1) Condenser Water System

        - Furnish and Install DDC Controller

        - Furnish and Install Outside Air Temperature

        - Furnish and Install Condenser Water Supply / Return Temperature Sensor

        - Furnish and Install Basin Water Temperature Sensor

        - Furnish Basin Heater Enable / Disable

        - Furnish Cooling Tower Fan Enable

        - Furnish Cooling Tower Fan Status

        - Furnish Cooling Tower VFD Control

        - Furnish Pump Start/ Stop and Status

        - Furnish Pump VFD Control

        - Furnish and Install Differential Pressure Transmitter

        - Furnish and Install Flow Meter

        - Furnish and Install BTU Meter – Flow Meter, Supply / Return Temperature Sensor

        - Tie in Mfr. Tower Vibration Switch

        - Tie in Mfr. High / Low Level Switch

        - Furnish and Wire Cooling Tower 10” Spray Isolation Valve and Actuator (Qty. 2 Total)

        - Furnish and Wire Cooling Tower 8” Sump Isolation Valve and Actuator (Qty. 2 Total)

        - Furnish and Wire Cooling Tower 10” Supply / Return Isolation Valve and Actuator (Qty. 4 Total)

        - Furnish and Wire DP Bypass Control Valve and Actuator

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

- (**tech hour: 2 hour each hardware point)

Qty (#) Electric - EUH / CUH / UH

        - Install and wire Space Thermostat (Furnished by Unit Mfr.)

- (**tech hour: 2 hour per each unit)

Qty (#) Electric Duct Heater EDH-#

        - Install and wire Duct Mounted Temperature Sensor (Furnished by Unit Mfr.)

        - Interlock with Associated Unit Operation

- (**tech hour: 2 hour per each unit)

Qty (#) Cabinet Unit Heater CUH-1

        - Furnish and Install DDC Controller or Communicating Thermostat

        - Furnish and Install Space Temperature Sensor

        - Furnish and Install Return Temperature Sensor

        - Furnish Fan Start / Stop and Status

        - Furnish and wire 3-Way Hot Water Control Valve and Actuator

- (**tech hour: 2 hour per each unit)

Qty (#) Water - EUH / CUH / UH

        - Install and wire Space Thermostat (Furnished by Unit Mfr.)

- OR

        - Furnish and Install BACnet Thermostat (when sequence / point list

        - Furnish and Wire Hot Water Control Valve and Actuator

- (**tech hour: 2 hour per each unit)

          - Qty (#) Air Curtain ACU-1 Thru 4

        - Install and wire Space Thermostat (Furnished by Unit Mfr.)

        - Interlock w/ Door Switch (Furnished by Unit Mfr.)

- (**tech hour: 2 hour per each unit)

- UV

Qty (#) Unit Ventilators UV-#

        - Furnish and Install DDC Controller

        - Furnish Fan Start / Stop and Status

        - Furnish and Install Space Temperature / Humidity / CO2

        - Furnish and Install Discharge Air Temperature

        - Furnish and Install Outside Air/Return Air Damper Actuator

        - Furnish and Install Freeze stat

        - Furnish and wire Hot Water Control Valve and Actuator

        - Necessary Control Wiring w/ Mfr. Provided Terminal Strip

- (**tech hour: 4 hour per each unit)

          - *Qty (16) Unit Ventilator UV-## / Qty (16) ACCU-## (DDC Ready)

        - Furnish and Install DDC Controller

        - Furnish and Install Space Temperature Sensor

        - Furnish and Wire Steam / Hot Water Control Valve and Actuator (by AME)

        - Furnish and Install Fan CT

        - Furnish and Install Leak Sensor

        - Furnish Needle Point Bipolar Ionization Status

        - Condenser Interlock Wiring

        - Tie-in mfr.  Provided Sensors and End-Devices via Terminal Strip

          - Damper Actuator

          - Freezestat

          - Discharge Air Temperature Sensor

          - Fan Relays

          - Steam / Hot Water Control Valve and Actuator (by mfr.)

- (**tech hour: 4 hour per each unit)

- **DDC Ready is the tricky part of the UV scope. Often what end devices are provided by unit mfr is detailed out in schedule and sequence of operation.

- **space Sensor is always by AME if DDC is provided by AME

          - Qty (4) Stair Pressurization Fans SPF-1-1/2, SPF-R-1/2

        - Furnish and Install DDC Controller

        - Furnish Fan Start / Stop and Status

        - Furnish Fan VFD control

        - Furnish and Install Stairwell Pressure Sensor

        - Furnish and Install Damper Actuator w/ End Switch

        - Furnish and Install Stairwell/Elevator Pressurization (Location: 6th Floor, 14th Floor)

- (**tech hour: 4 hour per each unit)

Qty (1) Fuel Oil Pump System

        - Necessary Control Wiring to / from Fuel Oil Management Panel

        - Furnish BMS Communication Wiring to Factory Controls

        - Map Available Points Via Mfr. Provided BMS Interface

- (**tech hour: 4 hour per each unit)

          - Misc Monitoring Systems

        - Map Available Points Via Mfr. Provided BMS Interface or Connect to Nearby DDC Controller

        - Gas meter (Furnished and Installed by Others)

            - Mfr. to Provide Pulse Output for Monitoring at BMS

        - Furnish and Install Electrical Meter

            - BMS Communication Wiring to Mfr. Provided BMS Interface

        - Make Up Water Alarming (Furnished by Unit Mfr.)

            - Mfr. to Provide Dry Contacts to Monitor Alarm at BMS

        - BTU Meter (Qty. #)

            - Supply / Return Temperature, Flow Meter

        - Fire Tank

            - Fire Tank Water Temperature

        - Fire Pump & Jockey Pump Common Fault Alarm Monitoring

        - Fire Alarm System Per Zone (Qty. #)

            - Trouble

            - Alarm

        - Sump Pit Level monitoring (Qty. #)

        - Emergency Generator

        - Emergency Generator Alarms

        - ATS monitoring (Minimum 4 Points) (Qty. #)

        - Furnish and Install Domestic Hot Water Flow Meter (Qty. 2)

        - UPS (Qty. ##)

        - Generator- Modbus Interface

        - Domestic Water Tank Level & Pump Status (Qty. ##)

        - Domestic Hot Water Heater(s) (Qty. ##)

        - Sewage Ejectors & Sump Pump(s) (Qty. ##)

        - Fire Alarm Interface-

            - Alarm condition for each floor, zone, unit and fan.

            - Smoke purge initiation command for each floor and/or zone.

            - Smoke control initiation command for each floor and/or zone

        - Sub Metering

            - Building Electric Meter for each area

            - Building Domestic Water Meter

            - Building Natural Gas Meter (Qty. ##)

            - Building Natural Gas Meter

        - Interface Lighting Control System (By Others) With Front End BMS Via Manufacturer Provided

- BMS Interface

- (**tech hour: 2 hour per triangle bullet and multiplied by qty.)

Qty (1) Global Points

        - Furnish and Install Outside Air Temperature

        - Furnish and Install Outside Air Humidity

        - Furnish and Install Outside Air CO2

        - Furnish Fire Alarm Active Alarm

- (**tech hour: 4 hour)

Furnish and Install Weather Station

- (**tech hour: 4 hour)

- Hot Water System

Qty (#) Boiler B-1, 2, 3, 4

Qty (#) Boiler Circulator Pump BP-1, 2, 3, 4

Qty (2) Hot Water Pump HWP-1, 2, 3

        - Furnish and Install DDC Controller

        - Furnish and Install Outside Air Temperature / Humidity Sensor

        - Furnish and Install Hot Water Supply / Return Temperature

        - Furnish Boiler Enable

        - Furnish Boiler Status

        - Furnish Boiler Alarm

        - Furnish Boiler Setpoint

        - Furnish Boiler Circulation Pump Start/ Stop and Status

        - Furnish Hot Water Pump Start/ Stop and Status

        - Furnish Hot Water Pump VFD Control

        - Furnish and Install Differential Pressure Transmitter

        - Furnish and Install Flow Meter

        - Furnish and Install Breakglass Switch / Station

        - Furnish and Install Flow Switch

        - Furnish and Install Boiler Room Natural Gas Sensor

        - Furnish and Install Boiler Room CO Sensor

        - Furnish and Install Horn and Strobe Sensor

        - Furnish and Install BTU Meter – Flow Meter, Supply / Return Temperature Sensor

        - Furnish and Install Intake / Exhaust Damper Actuator

        - Furnish and Wire Boiler Isolation Valve and Actuator

        - Furnish and Wire Heat Exchanger Control Valve and Actuator

        - Furnish and Install Expansion Tank Pressure Sensor

        - Boiler Trim Wiring

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

- (**tech hour: 2 hour per hardwired point)

          - Hot Water System

- Qty (3) Geothermal Heat Pump-2-1, 2, 3

- Qty (3) Hot Water Pump HWP-2-1, 2, 3

- Qty (2) Snow Melt Pump HGP-2-1, 2

- Qty (2) Expansion Tank ET-2-1, ET-2-2

- Qty (4) Plate Frame Heat Exchanger PFHX-2-3A, 3B; PFHX-2-4A, 4B

- Qty (2) ET-2-3, 4

- Qty (1) AS-2-3

        - Furnish and Install DDC Controller

        - Furnish and Install UPS for DDC Controller (As per Controls 5/M-818)

        - Furnish and Install GHP Heating Hot Water Temperature Transmitters (TT-39 thru TT-44) (Qty. 6 Total)

        - Furnish and Install Domestic Preheat Heat Exchanger Temperature Transmitters (TT-45 thru TT-48) (Qty. 4 Total)

        - Furnish and Install Snow Melt Heat Exchanger Temperature Transmitters (TT-49 thru TT-52) (Qty. 4 Total)

        - Furnish and Install Plant Heating Hot Water Supply Temperature Transmitter (TT-55) (Qty. 1 Total)

        - Furnish and Install Hot Glycol Supply Temperature Transmitter (TT-59) (Qty. 1 Total)

        - Furnish and Install Plant Hot Water Differential Pressure Transmitter (DPT-06) (Qty. 1 Total)

        - Furnish and Install Remote Hot Water Differential Pressure Transmitters (Roof - DPT-07 & DPT-08) (Qty. 2 Total)

        - Furnish and Install Snow Melt Differential Pressure Transmitter (2nd Floor - DPT-09) (Qty. 1 Total)

        - Furnish and Install Expansion Tank Pressure Transmitters (PT-04 & PT-05) (Qty. 2 Total)

        - Furnish and Install Domestic Preheat BTU Meter - Flow Meter, Temperature Transmitters (BTU-04, FT-06, TT-53, TT-54) (Qty. 1)

        - Furnish and Install Facility Hot Water BTU Meter - Flow Meter, Temperature Transmitters (BTU-05, FT-07, TT-56, TT-57) (Qty. 1)

        - Furnish and Install Snow Melt Hot Glycol BTU Meter - Flow Meter, Temperature Transmitters (BTU-06, FT-08, TT-58, TT-59) (Qty. 1)

        - Furnish and Install Hot Water System Make-Up Flow Transmitter (FT-09) (Qty. 1 Total)

        - Furnish and Install GHP Differential Pressure Sensors (DP-09, DP-10, DP-11) (Qty. 3 Total)

        - Furnish and Install GHP Flow Switches (FS-09, FS-10, FS-11) (Qty. 3 Total)

        - Furnish and Install PFHX Flow Meter (Qty. 4 Total) – as per detail

        - Furnish Pump Start/Stop and Status (Qty. 5 Total)

        - Furnish Pump VFD Control (Qty. 5 Total)

        - Furnish Pump VFD Feedback (Qty. 5 Total)

        - Furnish Pump VFD Common Alarm (Qty. 5 Total)

        - Furnish and Wire 4” GHP Hot Water Supply Control Valves and Actuators (MCV-10, MCV-11, MCV-12) (Qty. 3 Total)

        - Furnish and Wire 3” Domestic Water Preheat Control Valves and Actuators (MCV-13 & MCV-14) (Qty. 2 Total)

        - Furnish and Wire 4” Snow Melt Heat Exchanger Control Valves and Actuators (MCV-15 & MCV-16) (Qty. 2 Total)

        - Furnish and Wire Hot Water Plant Bypass Control Valve and Actuator (BPV-04) (Qty. 1 Total)

        - Furnish BMS Communication Wiring to Pump VFD Controls (Qty. 5 Total)

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

- (**tech hour: 2 hour per hardwired point)

- VRF / Split / CRAC / WSHP / Unit Ventilator

- 20-0404 – Nest Programmable Thermostat as alternate (Apartment / Hotel Jobs)

- VRF System

Qty (#) Indoor Unit AC

Qty (#) Condensing Unit ACCU

Qty (#) Branch Selector

        - Install and wire Programmable Thermostat (Furnished by Unit Mfr.)

        - Furnish and Install Remote Space Temperature Sensor

        - Furnish and Install Leak Sensor

        - Furnish and Install Local RAM Module

        - VRF Communication Wiring

        - Tie-in Condensate Pump Float Switch (Furnished by Mfr.)

        - Install Central Controller by Unit Mfr. Tie into BMS

          - AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

- OR

        - Furnish BMS Communication Wiring to Factory Controls

        - Map Available Points Via Mfr. Provided BMS Interface

          - AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

- (**tech hour: 2 hour per indoor unit)

Qty (#) Split System Indoor Unit CU- | Qty (#) Outdoor Unit ACCU-

        - Install and wire Programmable Thermostat (Furnished by Unit Mfr.)

        - Furnish and Install Space Temperature Sensor (BMS Monitoring)

        - Furnish and Install Leak Sensor

        - Furnish and Install Local RAM Module

        - Tie-in Condensate Pump Float Switch (Furnished by Mfr.)

        - Low Voltage Interlock Wiring between Indoor and Outdoor Unit

        - Furnish BMS Communication Wiring to Factory Controls

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

- (**tech hour: 2 hour per indoor unit)

Qty (#) Water Cooled Computer Room Air Conditioning Unit

        - Install and wire Programmable Thermostat (Furnished by Unit Mfr.)

        - Install and wire Space Temp/Humidity Sensor (Furnished by Unit Mfr.)

        - Furnish and Install Space Temperature Sensor for BMS Monitoring

        - Furnish and Install Leak Sensor

        - Furnish and Install Local RAM Module

        - Tie-in Condensate Pump Float Switch (Furnished by Mfr.)

        - Furnish and Wire Condenser Water Supply / Return Isolation Valve and Actuator

        - Condenser Interlock Wiring

        - Furnish BMS Communication Wiring to Factory Controls

        - Map Available Points Via Mfr. Provided BMS Interface

- AME requires mfr. Rep to assist in integration, cost to be incurred by mech contractor

- (**tech hour: 4 hour per indoor unit)

JOB SPECIFIC FEEDBACK

          - Qty (1) Unit Ventilator

        - Furnish and Install Outside Air Humidity Sensor (Individual sensor for each UV – for Eden engineering jobs)

          - VERIZON WORKSTATION BY VERIZON ITSELF

          - Qty (1) Daikin units for School Job

        - Get cutsheet from D&B for control information

        - Refer email ID: Estimating@dbbs.com

          - Qty (1) Guest Room Hotel Thermostat (Inncom)

        - It’s a Honeywell Product and AME will provide (25-0303 Feedback)

        - Get quote from Mark.McDade@inncom.com

          - Qty (1) for Packaged Controller + Bipolar on BMS

        - Tie-in Ionization Device Alarm

          - Qty (1) for AME DDC + Bipolar on BMS

        - Tie-in Ionization Device Alarm

          - Qty (1) Sky Spark Diagnostics (25-0258 feedback)

        - Add on the Top of the Proposal

        - Significant hours are added

          - Qty (1) VAV 24V Wiring

        - VAV Transformer by Unit Mfr. – if it shown on schedule / sequence / details

        - If VAV’s are not shown on electrical plans, but in electrical panel schedule then consider add alternate for 24V wiring scope

        - If VAV’s shown on electrical plans then 24v wiring by elec.

          - Qty (1) Balancing Scope

        - We only Assist for equipment balancing

          - Qty (1) Equipment VFD (When Mentioned its Interface to BMS)

        - Furnish BMS Communication Wiring to VFD Controls

        - Map Available Points Via Mfr. Provided BMS Interface

- AME Requires Mfr. Rep to Assist in Integration, cost to be Incurred by Mech Contractor

          - Qty (1) Furnish Niagara Analytics – If Called in Specs